  1. CHAPTER 1 INTRODUCTION National Thermal Power Corporation Ltd. (NTPC) was incorporated in 1975 by an Actof parliament, to supplement the efforts of the states for quicker and greater capacity additionin thermal power generation. In 1997, the Department of Public Enterprises, Government ofIndia granted ‘Navratna’ (Nine Jewels) status with powers of operational autonomy to theboard of NTPC with an objective to turn the public sector enterprise into a global giant. Thishas helped NTPC in speedy implementation of power projects, adoption of new technologiesand formation of Joint Ventures in the core generation as well as service businesses. Recently,NTPC has been awarded the „Maharatna’ status which has given it greater autonomy. In line with its vision and mission over the last thirty five years NTPC has grown tobecome the largest power utility in India with a commissioned generation capacity of 34,754MW (as on July, 2011) with power stations spread over the length and breadth of the country,covering portfolios in coal based and combined cycle power plants. Besides, being India‟s largest power generation utility, NTPC has also grown tobecome the number one independent power producer in Asia and second globally in 2009 (byPlatts, a division of McGraw-Hill companies), 5th largest company in Asia and 317th Largestcompany in the world (FORBES ranking – 2009) with Net Sales of Rs. 53721 crore during2010-11 as against Rs.46169 crore during 2009-10, as increase of 16.36% as on 31.03.2011.NTPC has also the honor of becoming the 6th largest thermal power generator in the world andsecond most efficient in terms of capacity utilization amongst top 10 utilities in the world. 1

  2. In line with the changing business environment, NTPC has expanded its operations inthe area of Hydro Power and covered substantial ground in the areas of Coal Mining, Oil &Gas Value Chain, Power Trading and Distribution. With these forward and backwardintegration plans, NTPC has been re-christened as “NTPC Limited” since 7th Nov, 2005. Today NTPC is more than a company. It is an institution, which has moulded theeconomy of India setting many landmarks particularly in Power Plant Engineering, Operationand Maintenance, Contract Management that other power organizations would strive toemulate. NTPC accepted the challenging task of taking over and running of the Ratnagiri Gas& Power Station (erstwhile Dabhol Power Plant). NTPC has drawn an ambitious programmeto become a 56000 plus MW Company by 2012 and 75000 plus MW Company by 2017.With a share of 17.75% in the total installed capacity in the country, NTPC‟s market share inthe country‟s power generation was 27.4% during FY 2010-11. 2

  3. Figure 1.1 Map Showing All NTPC Plants 3

  4. 1.1 LOCATION OF NTPC PLANTS WITH INSTALLED CAPACITY NTPC is having a number of Coal Fired Stations as well as Gas Fired Stationsthroughout the Country. Some of the Plants are constructed and run by NTPC in Joint Ventureswith other organizations.1.1.1 COAL STATIONS (OWNED BY NTPC) Figure 1.2 Coal Fired Stations owned by NTPC 4

  5. 1.1.2 GAS STATION (OWNED BY NTPC) Figure 1.3 Gas Stations owned by NTPC1.1.3 COAL STATION (IN JOINT VENTURE) Figure 1.4 Coal Fired Stations in JV 5

  6. 1.1.4 GAS STATION (IN JOINT VENTURE) Figure 1.5 Gas Station in JV1.2 FUTURE PLANS AND PERFORMANCE Figure 1.6 Future Plans 6

  7. Figure 1.7 Operating PLF: NTPC v/s All India Plants Figure 1.8 Generation v/s Capacity 7

  8. 1.3 NTPC’s MISSION AND VISION NTPC‟s vision and mission are driving force in all our endeavors to ultimately produceand deliver quality power in optimum cost and eco-friendly manner through concerted teamefforts and effective systems. Being an PSU, Anta has derived its mission and vision aligningwith that of the Corporate Mission and Vision.VISION: “A world class integrated power major, powering India’s growth, withincreasing global presence.”MISSION: “Develop and provide reliable power, related products and services atcompetitive prices, integrating multiple energy sources with innovative and eco-friendlytechnologies and contribute to society.”1.4 NTPC’s CORE VALUES The Core Values (BCOMIT), as of NTPC epitomizes the organizational culture and iscentral to every activity of the company. The values create involvement of all sections of theemployees. The core values are widely communicated for the actualization among theemployees. Business Ethics Customer Focus Organizational and Professional Pride Mutual Respect and Trust Innovation and Speed Total Quality for Excellence 8

  9. 1.5 ANTA GAS POWER STATION Rapid industrialization and growth in agriculture/domestic consumption of power in theNorth India was putting lot of strain on the power grid. To overcome the gap between supplyand demand, NTPC set up its first Gas Power Station at Anta. Presently NTPC, Anta is oneof the seven Gas Stations of NTPC. ANTA‟s journey towards excellence had started since inception. Today ANTA is oneof the best gas power plant in the country. It has achieved unique distinction of being the firstpower station of the country having Zero Forced Outage. ANTA is ISO 9001:2000, ISO14001:2004, OHSAS 18001:2007, SA 8000:2001 and FIVE-S certified.1.5.1 LOCATION AND ORIGIN With the findings of natural gas in Western Offshore fields of Bombay High, CentralGovernment decided to take this gas up to North India and accordingly lay the HBJ Pipelinestarting from Hazira. GOI directed to set up gas based combined cycle power plants alongwith HBJ pipeline. Initially 3 such projects were conceived at Anta, Kawas & Auraiya inStates of Rajasthan, Gujarat & UP respectively. Anta project was set up to mitigate the powershortage in the Northern region which was estimated between 13-16% of the peak demandduring the 7th plan period. Further, looking at the benefit of the low gestation, high efficiency,quick (Black) start and quick loading capability with mix-fuel flexibility and low pollutionimpact, Anta project was considered the most viable option to eminently fulfill the supplydemand gap in Northern Region. 9

  10. Figure 1.9 Location of NTPC, Anta1.5.2 BREIF PROFILE OF NTPC ANTA Station : Combined Cycle Gas Based Power Station Gas Turbines: 3 x 88.71 MW Steam Turbine: 1 x 153.2 MW Total Capacity : 419.33 MW Commercial Operation started w.e.f. 01.08.1990. 10

  11. 1.5.3 SALIENT FEATURES OF NTPC ANTA Figure 1.10 Salient features of NTPC Anta 11

  12. 1.6 PRODUCTS, SERVICES AND DELIVERY MECHANISM Sole product of NTPC-Anta is electrical power generated by using gas or naphtha as amain fuel. The generated power is transmitted through six 220 KV Lines. Thus NTPC‟s role islimited up to Switchyard, beyond which PGCIL network feeds to respective DISCOMs. Its customer consists of state distribution companies in member states of northern gridviz. Rajasthan, UP, Delhi, Punjab, Haryana, Himachal Pradesh, Uttaranchal, J&K andChandigarh. The coordination for generation scheduling is done by Anta with the NRLDC(Northern Region Load Dispatch Centre) of Power Grid located at New Delhi. Anta not onlyfulfils the customer requirements of adequate and reliable power at competitive price but alsoworks with the customer to maintain grid stability in the larger interest of the region. Tomaintain the grid stability, the supply and demand are to be consistently matched for which, thecommunication between the personnel manning the control room at Anta and the NRLDC isestablished on continuous basis. Figure 1.11 Allocation of Different States in Anta‟s Power 12

  13. 1.7 ORGANIZATIONAL HIERARCHY NTPC‟s current 3-tier structure comprises Corporate Centre (CMD, Board of Directorsand Corporate functions), Regional Head Quarters (five in numbers – NCR, NR, SR, ER andWR) and Stations/Projects, Anta being one of the stations. Anta falls under NCR-HQ. Thebusiness unit head of ANTA is the GENERAL MANAGER (GM). The power generation ishandled by Operations and Maintenance Department headed by AGM (O&M), reporting toGM. O&M consists of different sections viz. Operations, Mechanical Maintenance, ElectricalMaintenance, C&I Maintenance, Chemistry, EEMG, MTP, each sub section is headed by aDGM/Senior Manager. The support function departments viz. F&A, HR, Contracts &Materials, Safety, TQM, IT etc, headed by DGM/Senior Managers, are directly reporting to theGeneral Manager. Figure 1.12 Organization Chart of NTPC Anta 13

  14. 1.8 CORPORATE SOCIAL RESPONSIBILITY Anta is involved in many CSR activities like rural health check up camps, rural sports,school furnishing, vocational trainings etc. Anta employees and their family members areinvolved in various activities of CSR like voluntary services for education of villagers, help inemergency situations, eye camps, family planning camps etc. Photo 1.1 Night View of NTPC, Anta 14

  15. CHAPTER 2 TECHNOLOGY, EQUIPMENT AND FACILITIES ANTA is a combined cycle gas based power plant in which gas turbines operate onBrayton Cycle and steam turbine operates on Rankine Cycle. Anta has three Gas Turbineseach of 88.71 MW and one Steam Turbine of 153.2 MW. Total capacity is 419.33 MW. Themajor power generating equipments are of Alstom make. Apart from the plant, ANTA has anidyllic township “Kiran Kunj”. The township is equipped with all modern facilities viz.school, hospital, recreation centre, swimming pool, play grounds, parks, shopping complex,banks, post office, BSNL Exchange etc.2.1 POWER GENERATION PROCESS The Gas/Naphtha from pipeline is taken and supplied to GT Combustion Chamberwhere it is burnt as fuel along with air drawn from atmosphere. This heat is then convertedinto mechanical energy in the Gas Turbine. Gas turbine through a common shaft rotates aGenerator, which produces electric power. Flue gas from the turbine exhaust is used to convertwater into steam in the Waste Heat Recovery Boiler (WHRB). Water required for steamgeneration is circulated through the tubes in the boiler, where heat exchange takes place andwater gets converted into steam. The steam generated from WHRBs is used to run a steamturbo generator and produce electric power. This power is supplied to customer through 220KV lines. Photo 2.1 Birds Eye View of Plant 15

  16. 2.2 OVERVIEW OF COMBINED CYCLE Combined cycle power plant integrates two power conversion cycles with the principalobjective of increasing overall plant efficiency. Bratyon cycle (for gas turbine) Rankine cycle (for steam turbine) Let us have a look on How Combined Cycle works in a combined cycle power plant toincrease the efficiency of power generation process. Gas turbine exhaust is at temperature of 500-550 Celcius. Steam generation Process for Rankine cycle requires a temperature of 500-550 Celcius to generate steam. Gas turbine exhaust heat can be recovered using a waste heat recovery boiler to generate steam in a water tube boiler so as to run a steam turbine on Rankine cycle. Efficiency of simple gas turbine cycle is 34%. The efficiency of Rankine cycle is 35%. The overall efficiency of power generation by combined cycle comes to 49%. 16

  17. 2.2.1 GAS TURBINE Gas Turbine is a heat engine, working on the air standard Brayton cycle.The Process Includes:Compression: Compression of working medium (air) taken from atmosphere in a compressor.Combustion: Increase of working medium temperature by constant pressure ignition of fuel incombustion chamber.Expansion: Expansion of the product of combustion in a turbine.Rejection: Rejection of heat in the atmosphere. 17

  18. Figure 2.1 Simple Gas Turbine Cycle Figure 2.2 Line Diagram of Gas Turbine Cycle2.2.2 STEAM TURBINE Steam Turbine is a heat engine, working on Rankine cycle.The Process Includes:Pressurization: Pressurization of working medium (water) by Boiler feed water pump.Heating: Phase change of working medium (from water to steam) and superheating atconstant pressure in Boiler.Expansion: Expansion of the steam in a turbine. 18

  19. Condensation: Condensation of the steam by cooling water.2.3 GENERAL DESCRIPTION OF COMBINED CYCLE The 419.33MW anta combined cycle power plant consists of three gas turbinesgenerator sets of 88.71 MW each and one steam turbine generator set of 153.20 MW. The gasturbine are equipped with a dual fuel burner for gaseous fuel (natural) and liquid fuel(naphtha).the station can be operated in the open cycle mode via their exhaust gas bypassstacks or as modules together with their waste heat recovery boilers and STG in the combinedcycle mode. The WHRB‟s is designed as dual pressure boilers with high pressure (HP) and lowpressure (LP) sections and condensate preheating at the tail end. The condensate pumped fromthe condenser hot well is degasified in the Deaerator at constant pressure and stored in the feedwater tank. From feed water tank, the boiler feed water is extracted by mean of separate boilerfeed water pumps for the HP and LP system serving the 3 WHRB‟s in common HP and LPmain steam lines the turbojet is composed of a single flow HP turbine and one double flow LPturbine. The Generator is directly coupled to the shaft of LP cylinder. The exhaust steam of theSTG is condensed in a surface condenser cooled by fresh water of the right main Kota canal inthe once through cycle. During the shut-down of canal, the condenser is cooled via a wetcooling tower in the closed cycle alternatively. For start up and shut down as well as trip of STG one common HP and LP steambypass station for all 3 modules are provided leading the steam directly into the condenser.Additional steam charged air presenters are installed in front of the GT-compressor inlet topreheat the intake air for the gas turbine, improving the heat rate during part load operation. 19

  20. Photo 2.5 View of WHRB2.4 OVERVIEW OF GAS TURBINE A gas turbine plant in its most simple form consists of following main part. Air intake system Compressor Combustion chamber Turbine Generator Gas Fuel system Naphtha Fuel System 20

  21. Gas turbine plant operation2.4.1 AIR INTAKE SYSTEM Air enters the suction of compressor after passing through fine filters. There are 945filters arranged in three levels. These are self cleaning type filters. Compressed air from theinstrument air compressors passes through diaphragm valves and into the blowpipes. Apressure pulse is given to the filter elements in the reverse direction (inside to outside) thisimpulse of air flow cleans the filters. Make : FARR Material of filter media : Resin Impregnated Media consisting of synthetic and Cellulose fibers Total no. of filter cartridges : 945 Initiation of pulse cleaning : 6.4 m bar Stop of pulse cleaning cycle : 4.6 m bar Compressed air pulse clean : 7 bar Time interval bw two pulses : 30 sec. Time of a pulse : 0.1 sec. 21

  22. Figure 2.3 Air Intake Filters2.4.2 COMPRESSOR It is 18 stages with additional inlet guide blade, axial flow, reaction compressor. Theblade of the 18 rotor and 19 fixed rows are made of high tensile ferric chrome steel. The compressor casing is horizontally split at axis, and is made of spherical graphitecast iron. This material possesses high tensile strength and good expansion quality. Upper andlower halves of the compressor casing are provided with robust flanges and are held togetherby expansion studs with socket head. The compressor casing has three circular ducts at 4th,7th, 10th row of fixed blades. These ducts are closed to the outside by four bleed valves. Bleedvalves are kept open up to 2700 rpm, so that certain amount of compressor air can be blownoff. These bleed valves reduces the external power input required running compressor duringstart up.2.4.3 COMBUSTION CHAMBER In combustion chamber, the air compressed and supplied by compressor is brought tothe required process temperature by combustion of liquid/gas fuel. The single combustion 22

  23. chamber is fitted with only one dual fuel burner and mounted vertically on thecompressor/turbine assembly. The combustion chamber is all welded steel plate fabricated. The main parts are jacketwith cover, lower upper combustion chamber bodies, finned segment body, burner and innercasing. Combustion chamber jacket, which houses the components, is made of heat resistant,low alloy ferrite steel. The air from the compressor enter the combustion chamber from below and flowupward through the annular space between combustion chamber jacket and inner section of thelower combustion chamber body. Approximately 30% air flow enter the combustion chamberthrough eight mixing nozzles provided at the lower body as secondary and approximately30%air flow enter the combustion chamber through upper body via finned segment row (there are5row) , the remaining40%flow as primary air for combustion, into the swirl insert and enter thecombustion space with turbulence. After the fuel has ignited these gases are thoroughly mixedwith secondary air from mixing nozzles and brought to the permissible turbine inlet temp. 23

  24. Figure 2.4 Cross Sectional View of Gas turbine2.4.4 TURBINE Turbine is five stage reaction turbines. Due to high temperature of incoming gases, thefirst and second row of rotor and fixed blading are air cooled with air from compressordischarge. Cooling air passes along several holes made in blades and finally blowing outthrough numbers of slits in the trailing /leading edge of the blade. This method of coolingensures that blades are thoroughly cooled, thereby avoiding cracks induced by thermal stresses.These cooled blades are fixed rotor blades which are made of cast and nickel based alloy. Theturbine and compressor casing are bolted together at radial flange with expansion bolts, turbinecasing is made of heat resisting ferrite steel in order to with stand thermal stresses. 24

  25. 2.4.5 GENERATOR Photo 2.6 Generator Rotor Figure 2.5 Generator Data‟s Generator is three phases, two pole air cooled machine. The generator and turbine areplaced on common and plain concrete foundation, with same center line level for the turbineand generator rotor. 25

  26. The mechanical energy generated by turbine is converted to electrical energy by thegenerator and appear in the stator winding in the form of current and voltage. This balancesthe torque of the gas turbine. It lead the magnetic flux, and carries the field winding, the generator is self excited.The power required for the excitation is taken from the generator terminals and fed to the fieldwinding through the excitation transformer and the thrust-controlled rectifier units.2.4.6 GAS FUEL SYSTEM Gas comes from GRS at around 18 bars. Manual isolation valve is to be opened byoperator. Motorized stop relief valve will be opened by GT program when required. In the gas control block there is an emergency stop valve (ESV). This opens with thehelp of power oil pressure against spring force. Whenever turbine trips, the oil is drained(depressurized) and spring force closes the valve, cutting off gas supply to combustionchamber. After the ESV is the gas CV, the opening of this valve controls the amount of fuelgoing to the combustion chamber. 26

  27. 2.4.7 NAPHTHA FUEL SYSTEM Naphtha comes from naphtha station via the forwarding pumps at around 15bar.Manual isolation valve outside GT hall is to be opened by the operator. Manual isolationvalves before main fuel oil pump and also to be opened. Motorized valve will be opened by GTprogram when FG liquid fuel is selected. Naphtha then passes through duplex filter to the mainfuel oil pump, which raises the press to aproox.80 bar. There is release valve which openswhen firing speed is reached (600rpm). There is an emergency stop valve similar to one in the gas scheme. Finally there is thecontrol valve directly coupled with the Naphtha nozzle. A minimum opening of the nozzle isalready pre-set. Once stable flame is formed, the nozzle opening increases with the controlvalve opening.2.4.8 GAS TURBINE PLANT OPERATION The compressor sucks in air from the atmosphere through the filters called air intakefilters. The compresses air at approx. 11 bar passes into the combustion chamber where it isused as primary air for combustion and secondary air for cooling of very hot parts. The gasturbine generates the necessary power to drive the axial-flow compressor and the generator.Start-up of the GT is drives with the help of starting equipment which runs the generator as amotor with speed increasing from 0to 600 rpm. At this speed a pilot flame is ignited in thecombustion chamber, fuel (gas/naphtha) enters and combustion takes place. The speed increases further both with the help of generator motoring and thecombustion of fuel up to about 2000 rpm. At this speed starting equipment is switched off andonly the generator is made ready for synchronization with the grid. After synchronizations, the 27

  28. turbine load increases up to base load with more and more fuel entering the combustionchamber. The hot gases after combustion enter the gas turbine at about 1005 degree centigrade (atbase load). The higher pressure and temperature gas pass through the turbine rotating it andgenerator, this produces the electrical power. The exhaust gas coming out of the GT is at about 500 degree centigrade, this can beutilized to produce steam in WHRB.2.5 OVERVIEW OF WASTE HEAT RECOVERY BOILER Wagner-biro supplied boilers for anta combined cycle power plant known as waste heatrecovery boilers (WHRB), which are of non fired, dual pressure, forced circulation type. Theboiler has two different water/steam cycles known as high pressure system and low pressuresystem. Each system has its own boiler drum and circulating pumps, and is feed by HP & LPfeed water pumps from a common feed water tank. The HP&LP steam from the three boiler from four common headers HP live steam line,HP bypass line, LP live steam line and LP bypass line, the bypass line dump steam in thecondenser through the HP and LP bypass system. The HP steam drives the HP steam turbine through stop valves and control valves. TheLP steam after passing through stop valves and control valves mixes with the HP turbineexhaust and drivers the gas turbine. This dual system of operating utilizes the waste heavy 28

  29. from the gas turbine with maximum efficiency. From LP turbine steam enters the condenserwhere it get condensed to water with the help of cooling water .condenser is shell and tube,water flow through the tubes and steam flow out side. The condensate get collected in hot well,from hot well it enters the feed water tank through condensate. Each of the WHRB is feed with waste heat flue gas from the respective gas turbine(GT). The gas turbines are fired either with gas or naphtha. The energy from waste heat fluegas is transferred to water/steam by means of heating surfaces of super heaters, evaporators,economizers and condensate preheater. The steam-water system consists of a high (HP) andlow (LP) pressure system and in addition there is a condenser preheated in order to obtain ahigher efficiency.2.5.1 LP BOILER PART Economizer: The LP feed water, which flows from the 3 X 50% LP feed water pumps through the common feed water line to the WHRB‟s in parallel, enters a WHRB at economizer gate valve. In the economizer the feed water is heated up by the flue gas. After the economizer the feed water enters the LP boiler drum through feed regulating station (FRS), where the feed water control valve ensures the correct supply of feed water to the boiler. Boiler Drum Evaporator: The feed water in the LP boiler drum is pumped through the evaporator by means of 2 x 100% LP circulation pumps. In the evaporator the water is partially steamed by the flue gas passing at the outside of the evaporator tubes. The steam and water mixture again enters the drum, where steam is separated and this steam flows to the LP super heaters and the water is circulated again. LP Super Heater: The steam leaving at the top of the LP-drum flows through the flue gas heated super heater, where it reaches the end temperature of about 206 Centrigrade. 29

  30. 2.5.2 HP BOILER PART The principal design of the HP- boiler part is the same as for the LP- part. The basicdifference is of operating pressure. Economizer: The HP fed water, which flows from the 3 x 50% HP feed water pumps through the common the feed water line to the HP parts of 3 WHRB in parallel, enters a WHRB at the gate valve of economizer. This gate valve is equipped with a parallel bypass valve as in LP-economizer. Boiler Drum Evaporator: The feed water in the HP- boiler drum is pumped through the evaporator by means of 2 x 100% HP circulation pumps in the evaporator water is partially steamed as in LP part, this partially steamed water enters in HP drum where steam is separated, and water is circulated again. Theses steam is super heated in HP super heater. The HP circulation pumps ensure the correct water flow through evaporator for which differential pressure switches are provided. HP Super Heater: The HP super heater consists of two parts with a spray attemperator between them. This configuration allows the temperature control of the super heated steam. The spray water which is the cooling medium is branched from the feed water line at the HP economizer inlet via a control valve to the attemperator if the temperature of super heater increases beyond the predetermined temperature. Condensate Preheater: The main condensate is pumped by 3 x 50% condensate extraction pumps (CEP) to the feed water tank. Before entering the feed water tank the condensate is passed through the condensate preheaters which are situated at the tail end of the WHRB and heated by the flue gas to achieve the highest cycle efficiency. Blow down Tank: One blow down tank is provided for each WHRB to collect drains e.g. CBD, IBD and drum over flow water from hp and LP system of the WHRB. The water level in this tank is maintained through an over flow pipe, which leads the water to hot drain collecting system. The steam flows via a silencer to the atmosphere. 30

  31. 2.6 OVERVIEW OF STEAM TURBINE Photo 2.7 Steam Turbine Floor The steam turbine plant consists of a single shaft condensing turbo set with HP & LPlive steam admission and with HP & LP bypass steam system. The steam generating plantconsists of three waste heat recovery boilers (drum type) with common live steam lines.Exhaust gases of one appropriate gas turbine heat each boiler. Normally, the whole steam generated in boilers flows through the turbo set. Part ofsteam can be bled via extraction lines to preheat the intake air for gas turbines. After expansionin turbine, the remaining steam is condensed in the condenser. From there on, the condensate is 31

  32. fed through the gland steam condenser to a common feed water tank. The common HP & LPfeed water pumps supply the feed water to the three waste heat recovery boilers. The steam turbo set is composed of a single flow HP turbine and one double flow LPturbine arranged one after the other with tandem compounding. The HP turbine has 25 stagesand LP turbine has 2 x 6 stages of reaction blading. The generator is directly coupled to theshaft of the LP turbine. The cross over piping between the HP & LP brings the expanded steam of HP Turbineto the reaction blading in the LP turbine, where it expands down to the condenser pressure.2.6.1 HP TURBINE The high-pressure turbine is a single shell casing design. It consists of the turbinecasing, the fixed blade carriers, the dummy piston and the HP rotor.2.6.2 LP TURBINE The LP turbine is a double flow design .It consists of the welded turbine casing, thefixed blade carriers and the LP rotor. The LP casing is a welded fabrication from steel plate and is flanged together along thehorizontal plane at turbine axis height and LP rotor is a welded design mate of plain steel. 32

  33. CHAPTER 3 GENERATOR3.1 BASIC DESIGN AND TYPES Generators used in the power plants for the generation of electrical energy areSynchronous machines. Basically we have two types of generators depending upon the speedat which the machine is driven. These are: Turbo Generators driven by steam or gas turbines. Salient pole machines driven by hydraulic turbines or diesel engines and small steam turbines with gearing. Speed covers a wide range from 60 rpm to 1500 rpm depending on the number of poleschosen or the prevalent water condition (in hydraulic plants). The laminated stator core, with slots for the three-phase winding, is in principle thesame. The rotor, with the D.C supplied field windings, which generates the rotating field aredesigned in different ways: Salient pole with concentrated windings. Non salient pole with the field windings distributed in slots. 33

  34. 3.2 GENERATOR In a Generator, the magnetic field rotates as a consequence of the rotation of the rotor.This produces in the stator an alternating field, which induces voltage in the stator windings.Because of the alternating field the stator core must be composed of laminated stampings (i.e. alaminated stator core). The construction with the solid core would result in induced eddycurrents, which would dampen the field. Also the losses produced will be enormous. The stator has a three-phase winding and the three windings are displaced in air by 120and hence the voltages induced in the winding have a 120 phase shift. This equation gives the criteria for determining the basic dimensions of the generators. S = k A B d2 l n = c d2 l nS = rated apparent powerd = rotor diameterl = active lengthc = utilization factorHence we see that the power output solely depends upon the diameter and the length of therotor. Therefore if we need to increase the power output we can either increase the length orthe diameter. But in the present circumstances we cannot increase the diameter beyond acertain limit (due to the high speed of operation of the rotor) and hence the length goes up. Incase of the hydel power plants since the speed of operation is less we can afford to have largediameter of the rotor and hence the effective size reduces. 34

  35. 3.3 LOSSES IN THE GENERATOR3.3.1 CONSTANT LOSSES These are the kind of losses that are there even when neither the stator nor the rotorwindings are under voltage. This type of losses include Frictional losses in the bearings Windage losses in the gas Ventilation losses Losses in the seals where hydrogen is used for cooling3.3.2 VOLTAGE DEPENDENT LOSSES The iron loss of the laminated stator core is approximately proportional to the square ofthe flux density in the iron and hence also to the square of the voltage induced in the statorwindings. This induced voltage is slightly dependent on the load but we can assume it to beequal to the generator terminal voltage U P iron = U23.4 GENERATOR PROTECTION Generator protection comprises the protection of the Generator and its associatedelectrical circuitry as well as the equipment it is likely to influence. 35

  36. The protection basically protects Abnormal Running Conditions: Equipment, though entirely in order, can be overloaded. The overloading parameters can be current, voltage, frequency, temperature or saturation. Such abnormal running conditions, if allowed to continue, may well lead to a fault. Often it is possible to normalize such abnormalities after necessary alarm is initiated through protection. Fault Conditions: Here it is a must to isolate the faulty circuitry/equipment through protection to minimize the damage.3.5 MAJOR FAULTS Over-current Over-voltage Reverse Power Over temperature and Mechanical Danger Over-flux (Saturation) Earth Fault Protection Differential Protection 36

  37. 3.5.1 OVER CURRENT PROTECTION In general, over-current protection comprises of current transformers which step downthe primary current to lower value. The over-current protection is used in the generatorprotection as Back up protection at internal overloads and faults Main or back up protection at external faults3.5.2 OVER VOLTAGE PROTECTION In general, over-voltage protection comprises of voltage transformers which step downthe terminal voltage to lower value. The scaled down voltage is fed to the relay. The relaypicks up when the voltage value crosses its setting and isolates the circuit by opening therequired circuit breaker.3.5.3 REVERSE POWER PROTECTION The reverse power protection is for the protection of generators & specially its primemover against over speed.3.5.4 OVER TEMPERATURE AND MECHANICAL DANGER Continuous operation without input is not permissible for all types of prime movers ingeneral & steam turbine in particular because of the increased mechanical & thermal stresses to 37

  38. avoid mal-operation of this protection during load pick up after synchronization or sudden loadchange, small time delays are used.3.5.5 OVER FLUX PROTECTION The over-flux protection is meant to protect the magnetic circuits from saturation &overheating. Saturation is a phenomenon which occurs when magnetic intensity or loading ofthe machine exceeds the value for which the machine is designed for. Higher degree ofsaturation can cause overheating of magnetic circuits by increased magnetic circuit losses &can lead to mal-operation of differential protection by higher magnetizing current.3.5.6 EARTH FAULT PROTECTION Earth fault protection is the protection of electrical circuits against damage caused byearth fault. STATOR EARTH FAULT PROTECTION: The earth-fault is caused as a result of insulation breakdown. Inside a generator, even a small amount of earth-fault current for a considerable duration of time may lead to catastrophic failure as it results in gradual overheating of laminated iron in core causing short circuit in the lamination which results in further overheating of magnetic circuits. A great care is therefore taken to protect the generator from earth faults. STARTING EARTH FAULT: This protection is used only in case of GT Generator. This protection activates if an earth-fault occurs when the generator is on no load condition & yet to be synchronized i.e. Generator breaker is not closed. 38

  39. ROTOR EARTH FAULT PROTECTION: The rotor earth-fault protection is the protection of the rotor winding against earth-fault. The rotor winding is fed by DC excitation voltage which is not grounded. Hence, a single point earthing in rotor winding is not dangerous as no earth current can flow as no return path is there. This is the reason behind providing only alarm for a single point earthing in rotor winding. However, a second earth-fault at this point of time can be very damaging for the rotor & calls for immediate withdrawal of the generator from the grid.3.5.7 DIFFERENTIAL PROTECTION As the name implies, differential protection is the protection for difference in parameterof current. In any electrical system, each equipment shall be having incoming current &outgoing current. In normal condition, both of them shall be equal. However, whenever the equipment develop an internal fault, there will be a differencein the current parameters in magnitude depending on severity & type of the fault as well as itsexact location. The protection, seeing the difference, shall be activated & isolate theequipment. 39

  40. CHAPTER 4 TRANSFORMER The generator is connected to transformers by means of isolated bus ducts. Thistransformer is used to step up the generating voltage of 15.75 KV to grid voltage of 220 KV.This transformer is generally provided with OFAF cooling. It is also provided with off load /on load taps on the high voltage side. This transformer has elaborate cooling system consistingof number of oil pumps and cooling fans.4.1 SPECIFICATION OF GENERATOR TRANSFORMER Rated power 160 MVA KV (no load) HV 230 KV(no load)HV 15.75 Ampere HV 728 Amperes LV 10630.6 Phases 3 Frequency 50 Types of cooling OFAF (oil forced air forced ) Ambient oil temp O C 50 Ambient winding temp. O C 55 Connection Symbol Ynd11 Table 4.1 Specification of Generator Transformer 40

  41. 4.2 UNIT AUXILIARY TRANSFORMER The unit auxiliary transformer draws its input from the main bus duct connectinggenerator to the generator transformer. With higher unit ratings and higher steam conditions,the auxiliary power required also increases. For large units, it has become necessary to usemore than one auxiliary transformer. UAT‟s used at the plant are both tree winding and twowinding transformer. These UAT‟s are used to step down the voltage at two levels for differentworks. The 2.55 KV lines are used for the generator starting equipments while the 0.433 KVlines are used to operate the generator auxiliaries. Rated power 6300 MVA (5050 MVA + 1250 MVA) Rated voltage no load HV 15.75 KV Rated voltage no load LV side 2.55 KV and 0.433 KV Rated current HV side 230.9 A Rated voltage LV side 1143 A and 1667 A Frequency 50 Hz Vector symbol D,Y1,YN1 Table 4.2 Specification of UAT4.3 CAPACITIVE VOLTAGE TRANSFORMER It consists of a capacitive potential divider and an inductive medium voltage circuit.The CVT is useful for bilateral purposes to facilitate protection, metering and communicationin the high voltage system. The end of the bottom one capacitance is connected to the highfrequency (HF) point which further connects to the PLCC system which is to be used for the 41

  42. protection of the entire high voltage system and communication purpose as well . The otherend of the same capacitor is connected directly to the primary side of the transformer,immersed in the oil, and the transformed voltage is used for metering and control purpose.4.4 INTER CONNECTED TRANSFORMER These are single-phase auto transformer used to change the amplified generated voltageto different levels to feed the different power lines.4.5 CONSTRUCTIONAL DETAILS OF THE TRANSFORMER4.5.1 TANK It is of welded construction and fabricated from tested quality low carbon steel. Allseams and joints are factory welded. Tanks stiffeners are provided for general rigidity and aredesigned to prevent retention of water. It is designed to withstand: Mechanical shocks during transportations Vacuum filling of the oil Short circuit forces Tank shields are made up of magnetically permeable material so that no

magnetic fieldsshall exist outside the tank. 42

  43. 4.5.2 TANK COVER It is sloped to prevent retention of rain water. The tank cover is filled with pockets atthe position of max oil temp and winding temp indicators. All the bolted connections are fittedwith weather proof, hot oil resistant gaskets in between for complete oil tightness.4.5.3 PRESSURE RELIEF DEVICES This is provided for the rapid release of any pressure that may be generated in the tankand which may result in the damage of the equipment. It is mounted directly on the tank andoperates at static pressure of less than hydraulic test pressure of the tank.4.5.4 BUCHHOLZ RELAY A double float reed type Buchholz relay is provided. Any gas involved in thetransformer is collected in this relay. A copper / stainless steel tube may be connected from thegas collector to a valve located about 1200 mm above the ground level to facilitate samplingwith the transformer in service. The device is provided with two electrically independent ungrounded contacts; one foralarm for gas accumulation and the other for tripping on sudden rise of temperature. 43

  44. 4.5.5 CORE It is constructed from high grade non ageing cold rolled supper grain oriented siliconsteel lamination, known as HI-B. The core is designed so as to avoid static discharges,developments of short circuit paths within itself or to the earth clamping structures4.5.6 WINDINGS The windings of all 220 KV type transformer are made in dust proof, conditionedatmosphere. The insulation of the transformer windings and the connections are to be madefree from insulating compounds which are liable to soften, ooze out, shrink or collapse or arechemically active.4.5.7 INSULATING OIL Oil is used as coolant and dielectric.4.5.8 CONSERVATOR TANKS Conservator tank is designed such that the lower part acts as sump to meet therequirements of expansion of the total coil oil volume in the transformer. A valve is fitted atthe lowest point of the conservator for oiling and sampling. 44

  45. 4.5.9 SILICA GEL BREATHER The conservator is filled with dehydrating silica gel breather. The silica gel crystals inthe breather act as an indicator and turn pink from blue when they absorb moisture. Aftermajority of the crystals have turned pink the silica gel should be heated at around 150-200degree until the original color is obtained.4.5.10 TAP CHANGING EQUIPMENTS The transformer is provided with off circuit tap changing switch for varying itseffective ratio transformation while the transformer is de-energized.4.6 PROTECTIVE SCHEMES FOR POWER TRANSFORMERS A Power Transformer constitutes an important and expensive component in a powersystem. It is therefore essential to provide an efficient protective relay scheme to protect thetransformer from any severe damage which is likely to be caused by short circuited faultswithin the equipment itself or from any sustained overload or fault condition in the powersystems.4.6.1 RESTRICTED EARTH FAULT RELAY One of the schemes adopted for detection of earth fault in the transformer zone is arestricted earth fault relay system. In this method, each transformer winding will be provided 45

  46. with a current actuated relay. On the star connected side the relay responds to the balancebetween the values of zero sequence component of the phase currents and the neural current todiscriminate internal faults from external earth faults. On the delta side the relay is fed with theresidual current of the paralleled CTs in the 3 phases.4.6.2 BUCHHOLZ RELAY It is mainly a gas operated relay. It comprises two float elements fitted to the run of theoil pipe work from the top of the transformer tank to the conservator. The first float element isa gas detector alarm sounding element to trap any gases produced in the oil as a result of arcingat the point of fault, while the second element is a pressure sensing device responding to therush of oil in the pipe during a severe fault within the transformer tank.4.6.3 PRESSURE RELIEF DEVICE Transformer tank is a pressure vessel as the inside pressure can group steeply wheneverthere is a fault in the windings and the surrounding oil is suddenly vaporized. Tanks as such aretested for a pressure with stand capacity of 0.35 Kg/ cm2 to prevent bursting of the tank.4.6.4 BACK-UP PROTECTION Some form of time delay back up relay protection for large transformers are provided.Some of the common protective relay scheme for the transformer local back up protection ishighlighted below. 46

  47. Inverse Definite Minimum Time (I.D.M.T) Relay: The time of operation of this relay is depended upon the magnitude of the fault current, being comparatively long for low fault current and short for high fault current. Definite Time over Current Relay: In this method the relay has anadjustable definite time setting. Instantaneous Relay: This type of relay trips instantaneously without time delays as soon as it senses the fault.4.6.5 DIFFERENTIAL RELAY In this method, each transformer winding is provided with CT. A Differential Relay isconnected across the terminals of the CTs. In normal conditions direction of the currentsthrough both the CTs are same. Whenever there is a fault condition the direction of currentthrough one CT changes and the two current add up. The relay senses this large current andgives trip command. In this protection scheme the magnitude as well as the phases differencebetween the current of the two sides of the transformer is taken care of . The magnitude istaken care of by using the CT‟s of proper ratios (different on each side). The phases lag or leadis compensated by using another CT which has an opposite connection scheme ,ie, if thetransformer under consideration is a delta/ star transformer then we use a CT that I has star /delta scheme . 47

  48. 4.7 VARIOUS TESTS OF THE TRANSFORMER4.7.1 RATIO TEST This test is to test the transformation ratio of the transformer. To do this test we give asmall value of voltage at the HV side and measure the corresponding voltage at the LV side.We can then calculate the transformation ratio4.7.2 MAGNETIZING CURRENT TEST To test this we make use of a tongue tester. We apply a certain voltage at the primaryand test the corresponding value or current.4.7.3 PERCENTAGE IMPEDANCE TEST Here we calculate the P.U value of the impedance of the transformer winding. P.Uvalues are same for both LV and HV side.4.7.4 TEST FOR BDV (BREAK DOWN VOLTAGE) OF OIL It done to check the voltage at which the oil breaks down. Practically it should be atleast 40KV/mm. At NTPC this limit is set at 50 KV/mm. 48

  49. 4.7.5 TEST FOR MOISTURE CONTENT IN OIL The oil is tested for the amount of moisture in it, in the chemistry lab. Special care is tobe taken at the time of taking out the oil that is to be tested. The oil content should be < 100ppm. 49

  50. CHARACTER 5 POWER EVACUATION FROM NTPC ANTA Photo 5.1 Switchyard at NTPC Anta Anta Gas Power Project constructed by NTPC is located in Baran district of Rajasthan.The power generated is being sold to the beneficiary states of Northern Region. In order toevacuate power from this 4 GPP, it has been decided to construct 220 KV AC transmissionsystem based on the discussions with CEA. . 50

  51. The transmission system indicated in the Feasibility report is given as follows. 220KV D/C Anta-Bhilwara line 230 Km. 220KV D/C Anta-Dausa line 300 Km. Extension of 220 KV s/s of RSEB at Bhilwara and Dausa.5.1 SWITCHYARD 220 KV Switchyard is the place at which switching operation of power distribution isformed. All modern generating station uses a unit system of generation transformerconnection. This unit is connected through circuit breaker and isolated to the high frequencyvoltage bus. The output of generator is connected through high voltage side and low voltageside is connected to the bus.5.1.1 BUS BARS The bus bar arrangement is of single sectionalized bus bar. In this type of bus bars isdivided into two section connected by bus coupler. These buses are made of 2 ASCRconductor 250 mm. It has 6 feeders. There is more us which is known as auxiliary bus bas. 51

  52. 5.1.2 BUS COUPLER Bus coupler is used to couple two busses together. Bus coupler consists of a circuitbreaker and the isolator which are situated at both side of circuit breaker.5.1.3 CURRENT TRANSFORMER The current transformer is used with its primary winding connected in series with linecarrying the current to be measured. The primary winding consists of very few turn andtherefore there is no appropriate voltage drop across it. The secondary winding has largernumber of turns. Ammeter terminal is connected terminal. Thus a current transformer underSC condition the secondary rating current is 5A.5.1.4 POTENTIAL TRANSFORMER Potential transformer is used to operate the voltmeter the potential coil of volt meterand relays from high voltage lines. The primary winding is connected across the line/joiningcarrying the voltage to be measures. The secondary winding is so designed that the voltage of100V to 120 V is delivered to instrument load the normal secondary winding rating is 110 V.5.1.5 ISOLATING SWITCHWhenever the maintenance and repair work is carried out on equipment in a switchyard, it isdisconnected from a supply by the isolator. 52